## SG951 Luminaires
[7 empty] | External areas | [12 empty] | Luminaire requirements (Note 1) | [7 empty] | Control System requirements (Note 1)
Activity number (general) | Activity number (specific) | Department of Education "Official Room Usage" key words | Common activity name | Applicable Australian Standard (Note 2) | Table listing applicable recommendations | Australian Standard "Type of interior or Activity" | Australian Standard "Type of interior or activity" sub heading to be applied to suit room activity) Select applicable to room usage (Note 3) | Maintained average horizontal illuminance Ēh (lux) | Maintained point horizontal illuminance Ēph (lux) | Illuminance (horizontal uniformity) UE2 | Maintained point vertical illuminance Ēpv (lux) | Permissible luminaire type (managing upward waste light | Lamp colour appearance required for DET (k) | Lamp colour rendering (minimum) required for DET | Other recommendations and advice (DET) | Required operating life ≥ in hours to 70% of initial | Impact resistance ≥ | Tamper proof | Ingress protection ≥ | ESS Approved (not required for new build) | Integrated Dali option | Integrated Emergency option | Replaceable drivers and LEDS | CCTV Consideration | Other requirements including school specific comments | Constant light output | Daylight management (dusk to dawn) | Occupancy Sensing | Real Time Clock | Local Switching | Local Scene control | Remote management | Other control requirements
P11 | P11c | Covered Vehicle Area/Porte Cochere (external areas only, for internal areas see AS/NZS1680.2.1:2008 Table D1 Activity 11 all sections as applicable) | Driveways and car parks | AS/NZS 1158.3.1:2005 | 2.5 | Outdoor Car Parks | Low- Based on the highest value of either activity, occupancy and risk of crime | 3.5 | 0.7 | 10 | - | Types 3, 4, 5 or 6 | 4000 | Ra 70 or higher | Not applicable during daytime. Values only applicable when used at night | 50000 | IK08 | Y | IP 65 | Y | Y | N | Y | Y | N/A | N | Y | Y | N | N | N | N | N
P12 | P12 | Covered Vehicle Area/Porte Cochere (external areas only, for internal areas see AS/NZS1680.2.1:2008 Table D1 Activity 11 all sections as applicable) | Driveways and car parks - disabled spaces | AS/NZS 1158.3.1:2005 | 2.5 | Outdoor Car Parks | Designated parking spaces specifically intended for people with disabilities | - | ≥14 and ≥ Ēh | - | - | Types 3, 4, 5 or 7 | 4000 | Ra 70 or higher | Not applicable during daytime. Values only applicable when used at night | 50000 | IK08 | Y | IP 65 | Y | Y | N | Y | Y | N/A | N | Y | Y | N | N | N | N | N
P6 - P8 | P6 | External Movement | Walkways | AS/NZS 1158.3.1:2005 (referred by AS/NZS1680.5:2012) | 2.7 | Public activity areas (Generally pedestrian movement only) | High- Based on the highest value of either activity, need to enhance prestige and risk of crime | 21 | 7 | 10 | 7 | Types 2, 3, 4, 5 or 6 | 4000 | Ra 70 or higher | Not applicable during daytime. Values only applicable when used at night | 50000 | IK08 | Y | IP 65 | Y | Y | N | Y | Y | N/A | N | Y | Y | N | N | N | N | N
[7 empty] | Internal areas | [12 empty] | Luminaire requirements (Note 1) | [7 empty] | Control System requirements (Note 1)
Activity number (general) | Activity number (specific) | Department of Education "Official Room Usage" key words | Common activity name | Applicable Australian Standard (Note 2) | Table listing applicable recommendations | Australian Standard "Type of interior or Activity" | Australian Standard "Type of interior or activity" sub heading to be applied to suit room activity) Select applicable to room usage (Note 3) | Maintained illuminance (lux) | Lamp colour appearance required for DET (K) | Lamp colour rendering (minimum) required for DET | Maximum glare index | Uniformity U1 (Min/Avg) ≥ (Note 6) | Other recommendations and advice (DET) |  |  | Required operating life ≥ in hours to 70% of initial | Impact resistance ≥ | Tamper proof | Ingress protection ≥ | ESS Approved (not required for new build) | Integrated Dali option | Integrated Emergency option | Replaceable drivers and LEDS | CCTV Consideration | Other requirements including school specific comments | Constant light output | Daylight management (dusk to dawn) | Occupancy Sensing | Real Time Clock | Local Switching | Local Scene control | Remote management | Other control requirements
5 | 5.1 | Access Staff Shower/Toilet/Change, Access Student Shower/Toilet/Change, Performing Arts Change room, Shower | Change room | AS/NZS 1680.2.1:2008 | D1 | STAFF ROOMS | Changing rooms, locker rooms | 80 | 4000 | Ra 80 or higher | - | 0.5 |  |  |  | 50000 | IK 08 | N | IP 44 | Y | Y | Y | Y | N | N/A | N | N | Y to dim | N | N | N | N | N/A
4 | 4.2 | Food Technology L.S., Food/Research Space, Kitchen - Pre and Type 1 | Food technology learning space | AS/NZS 1680.2.1:2008 (referred by AS/NZS 1680.2.3:2008) | D1 | KITCHENS | Food preparation, cooking. washing up | 240 | 4000 | Ra 80 or higher | 22 | 0.5 0.7 | Luminaires must be HACCP compliant |  |  | 50000 | IK 04 | N | IP 44 | Y | Y | Y | Y | Y | N/A | Y | N | Y | Y | Y | Y | N | N/A
3 | 3.2 | Canteen, Student Canteen, Staff Kitchen, Tea Room | Kitchens | AS/NZS 1680.2.1:2008 | D1 | STAFF CANTEENS,CAFETERIA, DINING ROOMS | Counters | 240 | 4000 | Ra 80 or higher | - | 0.5 0.7 | Attention is drawn to the relevant health and safety regulations. |  |  | 50000 | IK 04 | N | IP 44 | Y | Y | Y | Y | Y | N/A | Y | N | Y | Y | Y | N | N | N/A
7 | N/A | Toilets, Shower | Toilets | AS/NZS 1680.2.1:2008 | D1 | TOILETS | N/A | 80 | 4000 | Ra 80 or higher | - | 0.5 |  |  |  | 50000 | IK 08 | Y | IP 44 | Y | Y | Y | Y | N | N/A | N | N | Y to dim | N | N | N | N | N/A
7 | 7.2 | Clerical/Printing, Duplicating Workroom, Printing/Photocopying | Print and copy rooms | AS/NZS 1680.2.2:2008 | E1 | Print room | Sustained, collating | 240 | 4000 | Ra 80 or higher | 19 | 0.5 0.7 |  |  |  | 50000 | N/A | N | IP4X | Y | Y | Y | Y | N | N/A | Y | N | Y to dim | N | Y | N | N | N/A
2 | 2.2 | Computer Learning Space, Computer Resource, Computer Room, Library computer work stations | Computer Learning areas | AS/NZS 1680.2.2:2008 | E1 | Screen based task areas | (b) Average detail | 320 | 4000 | Ra 80 or higher | 19 | 0.5 0.7 |  |  |  | 50000 | IK 04 | N | IP4X | Y | Y | Y | Y | Y | N/A | Y | N | Y | Y | Y | N | N | N/A
2 | 2.2 | Senior Study, Ancillary Staff, General Assistants, Staff Study, Common room, Staff Lounge, Resources | Staff rooms, Study rooms | AS/NZS 1680.2.2:2008 | E1 | Screen based task areas | (a) Good, simple | 240 | 4000 | Ra 80 or higher | 19 | 0.5 0.7 |  |  |  | 50000 | IK 04 | N | IP4X | Y | Y | Y | Y | N | N/A | Y | N | Y to dim | N | Y | N | N | N/A
2 | 2.2 2.3 | Office | Offices - All | AS/NZS 1680.2.2:2008 | E1 | Screen based task areas | Task (b) Average detail Background/environment | 320 160 | 4000 | Ra 80 or higher | 19 | 0.7 0.5 |  |  |  | 50000 | IK 00 | N | IP4X | Y | Y | Y | Y | N | N/A | Y | N | Y to dim | N | Y | N | N | N/A
6 | 6.4 6.7, 6.8 | Libraries | Libraries various areas | AS/NZS1680.2.3:2008 | D1 | Libraries | Book stacks, Reading areas Cataloguing, Circulation Desk | 240 320 | 4000 | Ra 80 or higher | 19 | 0.5 0.7 | Provide adequate vertical illumination to the face of stacks |  |  | 50000 | IK 00 | N | IP4X | Y | Y | Y | Y | Y | N/A | Y | N | Y | Y | Y | Y | N | N/A
5 | 5.3 | Meeting, Interview rooms (no screen based tasks) | Conference Rooms | AS/NZS 1680.2.2:2008 | E1 | Meeting Rooms | Conference Rooms | 240 (160) | 4000 | Ra 80 or higher | 19 | 0.5 0.7 |  |  |  | 50000 | IK00 | N | IP4X | Y | Y | Y | Y | N | N/A | Y | N | Y to dim | N | Y | N | N | N/A
1 | 1.2 | Student Reception, Student Waiting, Clinic Waiting | Waiting rooms | AS/NZS 1680.2.1:2008 | D1 | Entrances | Waiting rooms | 160 | 4000 | Ra 80 or higher | 19 | 0.5 0.7 | illuminance at floor level |  |  | 50000 | IK08 | N | IP4X | Y | Y | Y | Y | N | N/A | Y | N | N | Y | N | N | N | N/A
N/A | N/A | Uniform Shop | Uniform Shop | N/A | N/A | N/A | N/A | 320 | 4000 | Ra 80 or higher | 19 | 0.5 |  |  |  | 50000 | IK00 | N | IP4X | Y | Y | Y | Y | N | N/A | Y | N | Y | Y | Y | N | N | N/A
5 | 5.2 | Seminar, Training, Interview | Seminar rooms | AS/NZS 1680.2.2:2008 | E1 | MEETING ROOMS | Training rooms, seminar rooms | 240 | 4000 | Ra 80 or higher | 19 | 0.5 0.7 |  |  |  | 50000 | IK00 | N | IP4X | Y | Y | Y | Y | N | N/A | N
10 | 10 (a) | Control Room | Control rooms | AS/NZS1680.2.1:2008 | D1 | CONTROL AND MONITORING ROOMS | (a) Intermittently monitored | 240 | 4000 | Ra 80 or higher | - | 0.5 |  |  |  | 50000 | IK 04 | Y | IP 44 | Y | Y | Y | Y | N | N/A | N | N | N | N | Y | N | N | N/A
2 | 2.1 | Movement, Ramp | Corridors, passageways and ramps | AS/NZS1680.2.1:2008 | D1 | CIRCULATION AREAS | Corridors, passageways, ramps | 40 | 4000 | Ra 80 or higher | - | 0.3 | illuminance at floor level |  |  | 50000 | IK 08 | Y | IP 44 | Y | Y | Y | Y | Y | N/A | Y | N | Y to dim | N | N | N | N | N/A
1 | 1.1 | Entry, Reception | Foyers, entry areas | AS/NZS1680.2.1:2008 | D1 | ENTRANCES | Entrance halls, lobbies, foyers | 160 | 4000 | Ra 80 or higher | - | 0.3 | illuminance at floor level |  |  | 50000 | N/A | N | IP 44 | Y | Y | Y | Y | Y | N/A | Y | N | Y to dim | N | Y | N | N | N/A
2 | 2.3 | Lift | Lift | AS/NZS1680.2.1:2008 | D1 | CIRCULATION AREAS | Lifts. Escalators, moving walks | - | 4000 | Ra 80 or higher | - | 0.3 | See lighting requirements in the applicable Standard. either in the relevant part of the AS 1735 series or NZS 4332 |  |  | 50000 | IK 08 | Y | IP 44 | Y | Y | Y | Y | Y | N/A | N | N | Y to dim | N | N | N | N | N/A
9 | 9.1 9.2 | Plant Room, Communications Cupboard, Distribution Board, Dust extraction space, Mains Switch | Plant rooms | AS/NZS1680.2.1:2008 | D1 | PLANT ROOMS | General Control panels, switchboards | 80 160 | 4000 | Ra 80 or higher | 25 - | 0.5 |  |  |  | 30000 | IK 08 | N | IP 65 | Y | N | Y | Y | N | N/A | N | N | N | N | Y | N | N | N/A
2 | 2.2 | Stairs | Stairs internal and external | AS/NZS1680.2.1:2008 | D1 | CIRCULATION AREAS | Stairs (internal) | 80 | 4000 | Ra 80 or higher | - | 0.3 | External stairs should be lit to internal stair light levels when actively used at night |  |  | 50000 | IK 08 | Y | IP 65 | Y | Y | Y | Y | Y | N/A | N | Y | Y to dim | N | N | N | N | N/A
6 |  | Clinic, Sick Bay | Clinics First Aid rooms | AS/NZS1680.2.1:2008 | D1 | FIRST AID CENTRES | Rest rooms (First Aid) Treatment rooms | 40 320 | 4000 | Ra 90 or higher | - 19 | 0.5 |  |  |  | 50000 | N/A | Y | IP 44 | Y | Y | Y | Y | N | N/A | N | N | N | N | Y | N | N | N/A
8 | 8.2 (a) | Store | Store Rooms Irregular use | AS/NZS1680.2.1:2008 | D1 | STOREROOMS | Dead Storage | 80 | 4000 | Ra 80 or higher | - | 0.5 |  |  |  | 30000 | IK 04 | N | IP 44 | Y | Y | Y | N | N | N/A | N | N | N | N | Y | N | N | N/A
8 | 8.2 (b) | Store | Store Rooms Regular use | AS/NZS1680.2.1:2008 | D1 | STOREROOMS | Live Storage | 160 | 4000 | Ra 80 or higher | 25 | 0.5 |  |  |  | 30000 | IK 04 | N | IP 44 | Y | N | Y | N | N | N/A | N | N | N | N | Y | N | N | N/A
8 | 8.3 (b) | Chemical Store, Cleaning Store, LPG Store | Volatile materials stores | AS/NZS1680.2.1:2008 | D1 | STOREROOMS | Sustained tasks | 320 | 4000 | Ra 80 or higher | 25 | 0.5 | Consider explosion proof if appropriate |  |  | 30000 | IK 10 | Y | IP 65 | N | N | Y | N | Y | N/A | N | N | N | N | Y | N | N | N/A
1 2 | 1.2 2.4 | Breakout Area | Foyer General Learning Space | AS/NZS1680.2.3:2008 | D1 | AUDITORIUMS CLASSROOMS | Social activity General use | 80 240 | 4000 | Ra 80 or higher | 19 | 0.3 0.7 | Switching and dimming facilities are desirable Higher levels may be required depending on activity. |  |  | 50000 | IK 04 | N | IP 44 | Y | Y | Y | Y | Y | N/A | Y | N | Y to dim | Y | Y | Y where applicable | N | N/A
1 N/A | 1.2 N/A | Communal Space, Covered outdoor space, Multi-Purpose Space | Foyer Gymnasium | AS/NZS1680.2.3:2008 AS 2560.2.2 | D1 Table 2 | AUDITORIUMS MULTIPURPOSE SPORTS CENTRES | Social activity Recreation and training | 80 300 | 4000 | Ra 80 or higher | 19 See 6.1 of 2560.2.2 | 0.3 0.7 | Switching and dimming facilities are desirable Higher levels may be required depending on sporting activity or if competition |  |  | 50000 | IK 04 IK 10 | Y | IP 44 IP 65 | Y | Y | Y | Y | Y | N/A | Y | N | Y to dim | Y | Y | Y where applicable | N | N/A
1 | 1.4 | Stage, Performance Workshop, Performance Workspace, Raised Platform | Theatre and Stage | AS/NZS1680.2.3:2008 | D1 | AUDITORIUMS | Theatre use | Note 5 | Note 5 | Note 5 | Note 5 | Note 5 |  |  |  | Note 5 | Note 5 | Note 5 | Note 5 | Note 5 | Note 5 | Note 5 | Note 5 | Note 5 | Note 5 | Note 5 | Note 5 | Note 5 | Note 5 | Note 5 | Note 5 | Note 5 | Note 5
N/A | N/A | Fitness Laboratory | Fitness Classroom | AS2560.2.2 | Table 2 | MULTIPURPOSE SPORTS CENTRES | Recreation and training | 300 | 4000 | Ra 80 or higher | See 6.1 of 2560.2.2 | 0.7 |  |  |  | 50000 | IK 10 | N | IP 65 | Y | Y | Y | Y | N | N/A | Y | N | Y to dim | Y | Y | N | N | N/A
N/A | N/A | Gymnasium | Gymnasium | AS2560.2.2 | Table 2 | MULTIPURPOSE SPORTS CENTRES | Recreation and training | 300 | 4000 | Ra 80 or higher | See 6.1 of 2560.2.2 | 0.7 |  |  |  | 50000 | IK 10 | N | IP 65 | Y | Y | Y | Y | Y | N/A | Y | N | Y to dim | Y | Y | Y where applicable | N | N/A
2 | 2.4 | General, Shared, Tiered and Serviced Learning Spaces, Home Base, After School Care, Practical Activities | General classrooms | AS/NZS1680.2.3:2008 | D1 | CLASSROOMS | General use | 240 | 4000 | Ra 80 or higher | 19 | 0.5 0.7 |  |  |  | 50000 | IK 04 | N | IP 44 | Y | Y | Y | Y | N | N/A | Y | N | Y to dim | Y | Y | Y where applicable | N | N/A
2 | 2.8 | Special Learning Space, Special Programs Room | Special learning spaces | AS/NZS1680.2.3:2008 | D1 | CLASSROOMS | Reading rooms | 320 | 4000 | Ra 80 or higher | 19 | 0.5 0.7 |  |  |  | 50000 | IK 04 | N | IP 44 | Y | Y | Y | Y | N | N/A | Y | N | Y to dim | Y | Y | Y where applicable | N | N/A
2 | 2.5 | Laboratories and Preparation areas, Botany, Zoology, Darkrooms | Laboratories, Science classrooms | AS/NZS1680.2.3:2008 | D1 | CLASSROOMS | Laboratories | 320 | 4000 | Ra 80 or higher | 19 | 0.5 0.7 | Higher illuminances may he required depending on the nature of the laboratory tasks. In Darkrooms, special lighting may be required during film development |  |  | 50000 | IK 04 | N | IP 44 | Y | Y | Y | Y | Y | N/A | Y | N | Y to dim | Y | Y | Y where applicable | N | N/A
2 | 2.7 | Music Learning Space | Music | AS/NZS1680.2.3:2008 | D1 | CLASSROOMS | Music rooms | 320 | 4000 | Ra 80 or higher | 19 | 0.5 0.7 |  |  |  | 50000 | IK 04 | N | IP 44 | Y | Y | Y | Y | N | N/A | Y | N | Y to dim | Y | Y | Y where applicable | N | N/A
5 | 5.1 5.5 5.6 | Visual Arts Workshop, Art Learning Space, Kiln Room, Design and Technology Learning Spaces, Photographic Studio | Design and Art Spaces | AS/NZS1680.2.3:2008 | D1 | GRAPHIC DESIGN AND MATERIAL | Colour selection Layout and Artwork Photographs, moderate detail | 800 600 400 | 4000 | Ra 90 or higher | 19* | 0.5 0.7 | For colour matching, the spectral quality of the light source is important, The use of specially lit colour matching booths may be appropriate tor some tasks. Veiling reflections may occur on glass surfaces. |  |  | 50000 | IK 04 | N | IP 44 | Y | Y | Y | Y | N | N/A | Y | N | Y to dim | Y | Y | Y where applicable | N | N/A
6 | 6.2 | Audio Visual Workroom | A/V areas | AS/NZS1680.2.3:2008 | D1 | LIBRARY | Audio visual areas | 240 | 4000 | Ra 80 or higher | 19 | 0.5 0.7 |  |  |  | 50000 | IK 04 | N | IP 44 | Y | Y | Y | Y | N | N/A | Y | N | Y to dim | Y | Y | Y where applicable | N | N/A
9 | 9.1 9.2 9.3 9.4 | Materials / Technology Learning Space, Materials Workshop, Metal / Wood Technology Learning Space, Welding / Hot Metals Area, Workshops | Industrial Arts classrooms | AS/NZS1680.2.3:2008 | D1 | WORKSHOPS (Use tables according to activity) | Rough bench or machine work Medium bench work or machine work Fine bench or machine work Extra-fine bench or machine work | 240 400 800 1200 | 4000 | Ra 80 or higher | 22 19 19 19* | 0.5 0.7 | Supplementary local lighting may be desirable. Eye protection will be required for some activities. |  |  | 50000 | IK 08 | N | IP 44 | Y | Y | Y | Y | Y | N/A | Y | N | Y to dim | Y | Y | N | N | N/A
2 | 2.4 | Plant Space, Plant Growing Space (Note 4) | Horticulture | AS/NZS1680.2.3:2008 | D1 | CLASSROOM SPECIAL | General use | 240 | 4000 | Ra 80 or higher | 19 | 0.5 0.7 | Lighting specific to plant growth may be appropriate |  |  | 50000 | IK04 | N | IP 65 | Y | Y | Y | Y | N | N/A | Y | N | N | Y | Y | N | N | N/A
7 | 7.4 | Animal Space, Agriculture Covered Area, Growing/Breeding | Farm and Horticulture | AS/NZS 1680.2.4:2017 | E1 | ORDINARY VISUAL TASKS | Farm and rural buildings | 240 | 4000 | Ra 70 or higher |  | 0.5 0.7 | Lighting specific to plant growth may be appropriate |  |  | 50000 | IK 08 | N | IP 65 | Y | Y | Y | Y | Y | N/A | N | N | Y to dim | N | Y | N | N | N/A
7.2 | 7.2 | Laundry | Laundries | AS/NZS 1680.2.4:2017 | E1 | CLOTHING TEXTILE AND FOOTWEAR | Laundries and dry cleaning: receiving and dispatch, washing | 240 | 4000 | Ra 80 or higher | 22 | 0.5 0.7 |  |  |  | 50000 | IK 04 | N | IP 65 | Y | Y | Y | Y | Y | N/A | N | N | Y to dim | N | Y | N | N | N/A
Note 1: | These tables provide a general guide only. Certain locations and applications will require specific values different to those shown covering performance of lighting system, luminaires and control system. For example where vandalism is a known problem a higher IK rating may be required. Specific site by site and room by room clarifications should be sought prior to development of specific design solutions.
Note 2: | References to standards show main standard dates as at September 2018. All referenced standards must also be applied. All standards includes applicable amendments and subsequent updates which must also be applied. See all applicable notes and comments within standards.
Note 3: | Application of performance is entirely related to room use. Designers must ensure that the selection is appropriate on a room by room basis
Note 4: | Not specifically covered by standards. Suggested classification of space provided but actual usage should be considered.
Note 5: | Special application, see Clause 10.15.4 of standard. Specialist equipment to suit theatre use should be applied where applicable
Note 6: | Uniformity for rooms will often have 2 values. The general lighting system should deliver uniformity over the space of .5. Task areas will require .7
Note 7: | Outdoor learning areas or workshops are not in scope of standards if uncovered. If covered, see "General Learning Area" or "Workshop"